## Slide 1: Holistic Cost Analysis of Running a Computing Center Zhangqier Wang Throughput Computing 2025 June. 4th 2025

## Slide 2
Introduction
Holistic cost analysis on CMS T2
  Estimate the cost of each type of hardware
  Policy for procurement plan
Cost analysis for a general computing center
  A general way to form the policy
Outline

## Slide 3
The increasing volume of data (ex. HL-LHC), new physics exploration, and AI applications are driving a surge in computing resource requirements
Beyond performance metrics, more factors to consider
  Computing demand is increasing, leading to high power consumption
  Power consumption including cooling, a key contributor to operational expenses
  Low-power hardware advancements exist, but the cost-benefit of switching is unclear.
Introduction
Computing in general faces a major re-design to align with energy efficiency and sustainability goals.

## Slide 4
Hardware
Purchase
Racks: on average ~$5000/year
PUE = Total Facility Energy / IT Equipment Energy
Cost compositions
Cooling
Cost of computing is complicated, hardware purchase is just a fraction of it
  Including power usage, cooling, space usage.

## Slide 5: MIT Tier 2 Center
The MIT Tier-2 Center is a high-performance computing facility dedicated to processing, storing, and analyzing data for the CMS, LHCb, and other experiments
  Comprises approximately 700 machines, providing 25k CPU cores and 16.5 PB of storage.
  Compute/Storage mix model
Worker nodes are also used as storage devices
  Re-design to have dedicated compute and storage servers
MIT T2 site
Cost evaluation determine hardware retirement policy
  Prepare MIT T2 for HL-LHC (data x10)
  Improve energy efficiency
  Spend less to provide same amount of computation

## Slide 6: Holistic Cost Analysis on MIT T2

## Slide 7
CPU models categorized into 8 types
  power consumption, and cpu, memory usage are checked
  average year represents the age of the machine
Machine Categories
CPU model | Avg year | Production Process | HS06 | Cores | HS06/core
Intel(R)_Xeon(R)_E5310-5410 | 2008-2013 | 65 nm | 69 | 8 | 8.6
Intel(R)_Xeon(R)_X5647 | 2017 | 32 nm | 155 | 16 | 9.7
Intel(R)_Xeon(R)_E5520-5620 | 2018 | 45 nm | 120-140 | 16 | 8.1
Intel(R)_Xeon(R)_E5-series | 2018 | 14/22 nm | 169-449 | 8-40 | 11.1
Intel(R)_Xeon(R)_Silver | 2019 | 14 nm | 530-706 | 48-64 | 11.0
Intel(R)_Xeon(R)_Gold | 2021 | 10 nm | 904 | 64 | 14.1
AMD_EPYC_9754_128-Core_Processor | 2023 | 5 nm | 7450 | 512 | 14.6

## Slide 8
The power consumption is monitored using “ipmitool” and “omreport”.
The current is measured on two servers and compared to the current from the monitoring
  Measured using clamp meter and AC splitter
  Load CPUs using linux stress command “stress --cpu N --timeout 100”
  Load CPU with CMS actually process using 16/32 cores.
Power Cross-check
Current (A) |  | Base | 16 cpu | 32 cpu | 48 cpu | 64 cpu | CMS 16 cores | CMS 32 cores
Server1 | Meter | 2.80 | 3.72 | 4.44 | 4.63 | 4.81 | 4.07 | 5.00
 | Monitor | 2.8 | 3.8 | 4.4 | 4.6 | 4.8 | 4.0 | 5.0
Server2 | Meter | 2.49 | 3.44 | 4.13 | 4.37 | 4.49 | 3.76 | 4.64
 | monitor | 2.4 | 3.4 | 4.0 | 4.2 | 4.4 | 3.7 | 4.6
vs
Consistent current reading from monitoring and measurements

## Slide 9
MIT Tier 2 Power Usage
Power glitch
Power consumption is relatively stable for Tier 2 operation.
  Cost analysis based on data from the “plateau” region Nov.30th -Jan 15th

## Slide 10: MIT Tier 2 CPU usage
Memory usage extracted from active memory via ‘vmstats –s’
CPU usage and memory usage is highly correlated
  average 1.2 GB/core
No correlation found between power usage and disk activity
Power consumption and CPU usage is highly correlated.
Estimate the computing resource and its connection to the power consumption.
  Evaluated by Power/HS06
Power glitch
Power glitch

## Slide 11: CPU Usage Comparison
Old machines tend to be less used, due to job mismatches
  Intel(R)_Xeon(R)_E5310-5410 have only 8 cores per machine, no longer suitable for modern computation needs
  Production CMS pilots using 8 cores, CPU usage is very low for low core machines (fragmentation issue).
Good cpu utilization
consistent with CMS production
~16 cores
8 cores

## Slide 12: Power/Core Comparison
The average power consumption for delivering 1 computing core
cpu servers
high core >=48
Process node 10-14 nm

## Slide 13: Power/HS06 Comparison
The average power consumption for delivering 100 HS06 of compute
cpu servers
high core >=48
Process node 10-14 nm
>250 time less efficient compared to AMD cpu
A factor of 10 times due to low CPU efficiency
A factor of 25 times due to hardware power consumption

## Slide 14
T2 Total Power Usage
MIT CMS T2 is the major computing center running at the Site
There are other computing servers not accounted for
shutdown
measured T2 power

## Slide 15
T2 Total Power Usage
MIT CMS T2 is the major computing center running at the Site
  Scale T2 power to check overlay
overlay
Strong correlation in the T2 power usage vs site total power

## Slide 16: Example Cost Analysis
Translate power efficiency to cost efficiency
For each type of machines, the cost includes power, space, and cooling.
  Power price at T2: 14 – 18 cents / kWh
  Power usage effectiveness (PUE) is 1.4 as a typical example
  Space usage: >$5000 / (40 unit rack) every year
  Yearly cost = PUE * power * $0.16/kWh * year + $5000 * (rack space)
Cost of providing 100 HS06 computation
  Replace with new CPU server AMD_EPYC_9754 (5nm)
    Cost = $580 (purchase) + $42/year
    100 HS06 is provided by 1.9% of a single server
    Among $42 per year, $2.5 comes from rack usage, $40 comes from power bill.
  Intel(R)_Xeon(R)_E5310-5410 (65nm, >10 years old)
    Cost = $14,300/year
    If replaced, after 2 weeks it will break even
  Similar estimations for other CPU models

## Slide 17: Cost Summary
CPU type | Core/machine | Cost/100HS06 | “break even”
65 nm, >10 years | 8 | $14,300/year | 15 days
32/45 nm, >6 years old | 16 | $1,360/year | 5 months
14/22 nm, 6 years old | 30-40 | $411/year | 19 months
10/14 nm, < 5 years old | 48-64 | $185/year | 4 years
5nm | 512 | $42/year + $580 | -
5nm
10 nm
14 nm
14-22 nm
32-45 nm
65 nm
break even *: make a positive reform of investment

## Slide 18: Universal Cost Analysis Tool

## Slide 19
To Develop a tool to assess computing hardware and suggest cost-effective upgrades
  A Python package to analyze full cost of running existing computing hardware
Web interface to enter the parameters
Holistic cost analysis
Analyze hardware type
Evaluates performance and power consumption
Cost breakdowns in power, cooling, and racks
Fetch existing data base
Purchase of the new hardware to provide equivalent computing resources
  How much operation time to save money with new hardware
Upgrade recommendations to maintain performance at reduced cost.
Development of the Tool
CPU model
CPU usage
Power price
Site cooling system
Rack Type
Hardware details

## Slide 20
CPU usage pattern matters
  Pattern 1: constantly active with a CPU usage at certain level (like T2)
  Pattern 2: Active at high CPU usage, inactive at ~0 CPU usage
New hardware purchase
Parameters
  : HS score of a CPU model
  : Power consumption
  n: Units of a machine
  : CPU usage efficiency
  PUE: power usage effectiveness (cooling effectiveness)
  $5000: yearly spend of a rack
  : Maximum power supply of a rack
  Price: electric price in the unit of $/(W*year)
  T: time in unit year
is the price of AMD hardware: $30,000
Determined from data bases
Input parameters
Power bill
Rack price
Calculation

## Slide 21
Example of usage using MIT Tier 3 - 1000 Cores site
  Three types of hardware
CPU model | Process node | HS06 | Cores | Power @100% [W]
Intel(R)_Xeon(R)_E5430 | 65 nm | 69 | 8 | 260
Intel(R)_Xeon(R)_X5647/E5640 | 32 nm | 155 | 16 | 300
Intel(R)_Xeon(R)_E5-series | 22 nm | 355 | 32 | 360
Replace with new hardware ($30,000 each machine) |  |  |  | 
AMD 128-Core_Processor | 5 nm | 7450 | 512 | 1100
Cost for each type &
replacement recommendation
Input variable:
CPU average usage: 40%
Site power usage efficiency: 1.4
Power price 14 cents/kWh
Rack Type 12500W maximum
Replace
Optional
Keep
Real-World Application
CPU type | “break even” | Recommend
65 nm | 0.4 years | Replace
32 nm | 1.1 years | Optional
22 nm | 2.3 years | Keep

## Slide 22
Holistic Cost Analysis is presented for running a computing center
  Cost from the power consumption can be enormous, strongly depends on the hardware and age
    Smaller computing setups can draw substantial amount of power
Old hardware should be replaced to reduce long-term operational costs
A rough guideline
  Hardware older than 10 years should be replaced immediately
  Hardware older than 7 years should be replaced
    A node with >30 nm process
    Cost savings typically realized within 1–2 years.
Provide a general tool/way to conduct the cost analysis
Summary
The End

## Slide 23: Back up

## Slide 24
Machines with the same CPU model may be produced in different years and have been running longer.
  Aging effect on power consumption is checked
Check the power usage on 3 CPU models
  Intel(R)_Xeon(R)_Silver_4116_2.10GHz: 104 machines (2018-2019), 2 machines (2021-2023)
  Intel(R)_Xeon(R)_Gold_6326_2.90GHz: 36 machines (2021), 22 machines (2022)
  Intel(R)_Xeon(R)_X5647_2.93GHz: 2 machines (2011-2012), 63 machines (2017)
Machine Age
As expected, no degradation observed over the years

## Slide 25: HS06 Comparison
The average HS06 per machine